## Sheet1
Estimate
Name of work:- Providing electrical points with allied works in two rooms adjoined to recently built lab space on terrace of 2nd floor New Core Lab. in Academic area in the campus at IIT Kanpur.
S. No. | Description | Qty. | Unit | Rate | Amount (Rs.) | Base (DSR 2022 & MR)
1 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. |  |  |  |  | 1.3
a) | Group C | 19 | Points | 1845 | 35055 | 1.3.3
2 | Wiring for group controlled (looped) light point/fan point/exhaust fan point/ call bell point (without independent switch etc.) with 1.5 sq. mm ERLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit, and earthing the point with 1.5 sq. mm ERLS PVC insulated copper conductor single core cable etc. as required. |  |  |  |  | 1.54
a) | Group C | 5 | Point | 1094 | 5470 | 1.54.3
3 | Supplying & drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel / PVC conduit as reqd.
a) | 1 x 1.5 sq. mm | 10 | Mtr. | 45 | 450 | 1.17.1
b) | 3 x 1.5 Sq.mm.. | 20 | Mtr. | 95 | 1900 | 1.17.3
c) | 3 x 2.5 Sq.mm.. | 20 | Mtr. | 137 | 2740 | 1.17.12
d) | 3 x 4 Sq.mm.. | 40 | Mtr. | 206 | 8240 | 1.17.21
e) | 3 x 6 Sq.mm | 40 | Mtr. | 304 | 12160 | 1.17.30
f) | 6 x 10 Sq.mm.. | 40 | Mtr. | 1219 | 48760 | MR
3 | Supplying and drawing following pair 0.5 mm dia FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. |  |  |  |  | 1.18
a) | 2 Pair | 80 | Mtr. | 38 | 3040 | 1.18.2
4 | Supplying and fixing of following size of steel conduit along with the accessories in surface/recess I/c painting in case of surface conduit or cutting the wall and making good the same in case of recessed conduit. as reqd. |  |  |  |  | 1.2
a) | 20 mm | 50 | Mtr. | 223 | 11150 | 1.20.1
b) | 25 mm | 30 | Mtr. | 256 | 7680 | 1.20.2
c) | 32 mm | 20 | Mtr. | 326 | 6520 | 1.20.3
5 | Supply, fixing, following modular type switch / socket on existing modular plate & switch box including connectins but excluding modular plate etc. as reqd. |  |  |  |  | 1.24
a) | 5/6 A switch | 30 | No. | 103 | 3090 | 1.24.1
b) | 2 way 5/6 A switch | 2 | No. | 148 | 296 | 1.24.2
c) | 15/16 A switch | 2 | No. | 156 | 312 | 1.24.3
d) | 3 pin 5/6 A socket outlet | 3 | No. | 122 | 366 | 1.24.4
e) | 6 pin 15/16 A socket outlet | 2 | No. | 197 | 394 | 1.24.5
f) | Telephone socket outlet | 2 | No. | 148 | 296 | 1.24.6
g) | Blanking Plate | 5 | No. | 40 | 200 | 1.26
h) | two module stepped type electronic fan regulator | 8 | No. | 369 | 2952 | 1.25
6 | Supplying and fixing following size/ modules, Gl box alongwith modular base & cover plate for modular switches in recess etc. as required. |  |  |  |  | 1.27
a) | 1 or 2 Module (75mmX75mm) | 8 | No. | 298 | 2384 | 1.27.1
b) | 3 Module (100mmX75mm) | 8 | No. | 327 | 2616 | 1.27.2
c) | 4 Module (125mmX75mm) | 1 | No. | 343 | 343 | 1.27.3
d) | 6 Module (200mmX75mm) | 20 | No. | 402 | 8040 | 1.27.4
e) | 8 Module (125mmX125mm) | 4 | No. | 454 | 1816 | 1.27.5
7 | Supplying and fixing following modular base & cover plate on existing modular metal boxes etc. as reqd. |  |  |  |  | 1.28
a) | lor 2 Module | 2 | No. | 133 | 266 | 1.28.1
b) | 3 Module | 2 | No. | 151 | 302 | 1.28.2
c) | 4 Module | 1 | No. | 158 | 158 | 1.28.3
d) | 6 Module | 1 | No. | 182 | 182 | 1.28.4
e) | 8 Module | 1 | No. | 211 | 211 | 1.28.5
8 | Supplying and fixing 3 pin, 5 A ceiling rose on the existing junction box/ wooden block including connections etc. as required. | 24 | No. | 87 | 2088 | 1.33
9 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) |  |  |  |  | 2.4
a) | 8 way (4 + 24), Double door | 2 | No. | 5967 | 11934 | 2.4.3
10 | Supplying and fixing 5 amps to 32 amps rating, 240 volts, 'C' series, MCB suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as reqd. |  |  |  |  | 2.1
a) | Single Pole | 16 | Nos. | 256 | 4096 | 2.10.1
b) | Single Pole & Neutral | 2 | Nos. | 599 | 1198 | 2.10.2
c) | Triple pole | 1 | No. | 1007 | 1007 | 2.10.4
d) | Triple pole and neutral | 1 | No. | 1228 | 1228 | 2.10.5
e) | blanking plate | 10 | No. | 13 | 130 | 2.11
11 | Supplying and fixing following rating, double pole, (single phaseand neutral), 240 V, residual current circuit breaker (RCCB), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  | 0 | 2.14
a) | 40 A | 6 | No. | 2642 | 15852 | 2.14.2
12 | Supply, Installation, Testing and Commissioning of 1200 mm sweep, BEE 5 star rated, ceiling fan with Brush Less Direct Current (BLDC) Motor, class of insulation: B, 3 nos. blades, 30 cm long down rod, 2 nos. canopies, shackle kit, safety rope, copper winding, Power Factor not less than 0.9, Service Value (CMM/W) minimum 6.85, Air delivery minimum 215 CMM, 350 RPM (tolerance as per IS : 374- 2019), THD less than 10%, remote or electronic regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise=75 degree C (max.), insulation resistance more than 2 mega ohm, suitable for 230 V, 50 Hz, single phase AC Supply, earthing etc. complete as required. | 8 | Nos. | 2730 | 21840 | 19.1
13 | Providing and fixing M.S. fan clamp type I or II of 16 mm dia M.S. bar,bent to shape with hooked ends in R.C.C. slabs or beams during laying,including painting the exposed portion of loop,all as per standard design complete. | 8 | Nos. | 226 | 1808 | 10.17 Civil
14 | S & F 40 amp to 63 amp rating 240 volts 'C' curve 10 kA MCB of following pole in the existing MCB DB complete with connection, testing & commissioning etc as reqd. ( legrand) |  |  |  |  | MR
a) | Triple pole and neutral | 2 | Nos. | 3637 | 7274 | MR
15 | Supply fixing connecting & commissioning of following rating 3 pin Plug top as reqd complete.
a) | 15/16 Amp | 1 | Nos. | 151 | 151 | MR
16 | Laying UTP cable enhanced cat 5/cat 6 cable in existing steel conduit pipe/GI pipe/ raceway / RCC pipe as reqd. the cost shall also include numbering of networking wire from room to rack as reqd. (wire will be supplied by dept) | 800 | Mtr. | 23 | 18400 | MR
17 | Fixing of RJ-45 modular box with cover plate or I/o box for internet on surface/ recessed cutting the wall making good the same as required. ( box and cover plate will be supplied by dept.) | 20 | Nos. | 96 | 1920 | MR
18 | Providing and fixing DLP plastic trunking of size 105 mm x 50 mm without cover on surface as reqd. | 30 | Mtr. | 1157 | 34710 | MR
19 | Providing and fixing DLP plastic trunking of size 105 mm x 50 mm accessories on surface as reqd.
a) | PVC trunking full cover of size 85 mm size | 30 | Mtr. | 510 | 15300 | MR
b) | End cap | 4 | Nos. | 231 | 924 | MR
c) | Internal angle. | 5 | Nos. | 638 | 3190 | MR
d) | External angle | 5 | Nos. | 653 | 3265 | MR
e) | flat angle | 1 | Nos. | 902 | 902 | MR
f) | cover joint | 10 | Nos. | 265 | 2650 | MR
g) | Base joint | 60 | Nos. | 106 | 6360 | MR
h) | separation partitions | 1 | Mtr | 305 | 305 | MR
i) | flat junction | 1 | Nos. | 1111 | 1111 | MR
20 | Supplying, installation DLP mini- trunking 32mm x 20mm and accessories white-system with independent cover- without central partion etc. as reqd.
a) | Mini- trunking | 100 | Mtr. | 268 | 26800 | MR
b) | End cap left or right | 50 | Nos. | 179 | 8950 | MR
c) | Internal/ external angle | 60 | Nos. | 173 | 10380 | MR
d) | Flat angle | 40 | Nos. | 145 | 5800 | MR
e) | Flat junction | 20 | Nos. | 171 | 3420 | MR
21 | Supply and installation testing and commissioning of following LED fitting surface/recess mounted, IP20, with metallic CRCA powder coated housing cover highefficiency diffuser, THD less than10, power factor above 0.9.etc. as required Crompton make.
a) | 12W LED light 1"X1" or round cat no. LCDSPLN-R-12-CDL | 2 | Nos. | 1620 | 3240 | MR
b) | 36W LED light 2"X2" cat no. LCTLSNE-36-FO-CDL | 16 | Nos. | 6235 | 99760 | MR
22 | Supplying, fixing, connecting, commissioning and testing of the following luminaries light fixtures complete with all accessories and with lamp as required complete. |  |  |  |  | MR
a) | LED tube light fitting (1 X 18 / 20 Watt. LED) surface mounting luminares | 2 | Nos. | 1030 | 2060 | MR
23 | Supplying and fixing following size/ modules, Plastic/ PVC box alongwith modular base & cover plate for modular switches in recess etc. as required. Make- legrand. |  |  |  |  | MR
a) | 1/2 module (75mm X 75mm) | 8 | Nos. | 403 | 3224 | MR
b) | 3 module (100mm X 75mm) | 8 | Nos. | 443 | 3544 | MR
c) | 4 module (125mm X 75mm) | 1 | Nos. | 478 | 478 | MR
d) | 6 module (200mm X 75mm) | 3 | Nos. | 541 | 1623 | MR
e) | 8 module (125mm X 125mm) | 2 | Nos. | 598 | 1196 | MR
24 | S & F of following size of steel flexible pipe alongwith the accessories on surface/open duct as required. .
a) | 20mm | 10 | Mtr | 81 | 810 | MR
a) | 25mm | 5 | Mtr | 95 | 475 | MR
a) | 32mm | 3 | Mtr | 116 | 348 | MR
25 | S&F, Copper tube / reducer/ lug terminals suitable for following size of conductor. |  |  |  |  | MR
a) | 6,10,16 mm | 30 | Nos. | 49 | 1470 | MR
| Total DSR & MR Items |  |  |  | 498610
| Without GST |  |  |  | 437185.445
| Add GST @ 18% |  |  |  | 78693.3801
| Total |  |  |  | 515878.8251
| Add contingency @3% |  |  |  | 15476.3648
| Grand Total Rs |  |  |  | 531355.1898
| Say Rs. |  |  |  | 531355

## Sheet2
Name of work:- Providing electrical points with allied works in two rooms adjoined to recently built lab space on terrace of 2nd floor New Core Lab. in Academic area in the campus at IIT Kanpur
S.No | Description | Qty. | Unit | Rate | Amount (Rs.)
1 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
1.1 | Group C | 19 | Points | 1845 | 35055 | 1620 | 30780
2 | Wiring for group controlled (looped) light point/fan point/exhaust fan point/ call bell point (without independent switch etc.) with 1.5 sq. mm ERLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit, and earthing the point with 1.5 sq. mm ERLS PVC insulated copper conductor single core cable etc. as required.
2.1 | Group C | 5 | Point | 1094 | 5470 | 960 | 4800
3 | Supplying & drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel / PVC conduit as reqd.
3.1 | 1 x 1.5 sq. mm | 10 | Mtr. | 45 | 450 | 39 | 390
3.2 | 3 x 1.5 Sq.mm.. | 20 | Mtr. | 95 | 1900 | 83 | 1660
3.3 | 3 x 2.5 Sq.mm.. | 20 | Mtr. | 137 | 2740 | 120 | 2400
3.4 | 3 x 4 Sq.mm.. | 40 | Mtr. | 206 | 8240 | 181 | 7240
3.5 | 3 x 6 Sq.mm | 40 | Mtr. | 304 | 12160 | 266 | 10640
3.6 | 6 x 10 Sq.mm.. | 40 | Mtr. | 1219 | 48760 | 1068 | 42720
4 | Supplying and drawing following pair 0.5 mm dia FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required.
4.1 | 2 Pair | 80 | Mtr. | 38 | 3040 | 35 | 2800
5 | Supplying and fixing of following size of steel conduit along with the accessories in surface/recess I/c painting in case of surface conduit or cutting the wall and making good the same in case of recessed conduit. as reqd.
5.1 | 20 mm | 50 | Mtr. | 223 | 11150 | 196 | 9800
5.2 | 25 mm | 30 | Mtr. | 256 | 7680 | 224 | 6720
5.3 | 32 mm | 20 | Mtr. | 326 | 6520 | 285 | 5700
6 | Supply, fixing, following modular type switch / socket on existing modular plate & switch box including connectins but excluding modular plate etc. as reqd.
6.1 | 5/6 A switch | 30 | No. | 103 | 3090 | 90 | 2700
6.2 | 2 way 5/6 A switch | 2 | No. | 148 | 296 | 19 | 38
6.3 | 15/16 A switch | 2 | No. | 156 | 312 | 136 | 272
6.4 | 3 pin 5/6 A socket outlet | 3 | No. | 122 | 366 | 107 | 321
6.5 | 6 pin 15/16 A socket outlet | 2 | No. | 197 | 394 | 173 | 346
6.6 | Telephone socket outlet | 2 | No. | 148 | 296 | 130 | 260
6.7 | Blanking Plate | 5 | No. | 40 | 200 | 35 | 175
6.8 | two module stepped type electronic fan regulator | 8 | No. | 369 | 2952 | 324 | 2592
7 | Supplying and fixing following size/ modules, Gl box alongwith modular base & cover plate for modular switches in recess etc. as required.
7.1 | 1 or 2 Module (75mmX75mm) | 8 | No. | 298 | 2384 | 261 | 2088
7.2 | 3 Module (100mmX75mm) | 8 | No. | 327 | 2616 | 286 | 2288
7.3 | 4 Module (125mmX75mm) | 1 | No. | 343 | 343 | 300 | 300
7.4 | 6 Module (200mmX75mm) | 20 | No. | 402 | 8040 | 352 | 7040
7.5 | 8 Module (125mmX125mm) | 4 | No. | 454 | 1816 | 398 | 1592
8 | Supplying and fixing following modular base & cover plate on existing modular metal boxes etc. as reqd.
8.1 | lor 2 Module | 2 | No. | 133 | 266 | 116 | 232
8.2 | 3 Module | 2 | No. | 151 | 302 | 132 | 264
8.3 | 4 Module | 1 | No. | 158 | 158 | 139 | 139
8.4 | 6 Module | 1 | No. | 182 | 182 | 159 | 159
8.5 | 8 Module | 1 | No. | 211 | 211 | 185 | 185
9 | Supplying and fixing 3 pin, 5 A ceiling rose on the existing junction box/ wooden block including connections etc. as required. | 24 | No. | 87 | 2088 | 76 | 1824
10 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
10.1 | 8 way (4 + 24), Double door | 2 | No. | 5967 | 11934 | 5231 | 10462
11 | Supplying and fixing 5 amps to 32 amps rating, 240 volts, 'C' series, MCB suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as reqd.
11.1 | Single Pole | 16 | Nos. | 256 | 4096 | 224 | 3584
11.2 | Single Pole & Neutral | 2 | Nos. | 599 | 1198 | 525 | 1050
11.3 | Triple pole | 1 | No. | 1007 | 1007 | 882 | 882
11.4 | Triple pole and neutral | 1 | No. | 1228 | 1228 | 1076 | 1076
11.5 | blanking plate | 10 | No. | 13 | 130 | 11 | 110
12 | Supplying and fixing following rating, double pole, (single phaseand neutral), 240 V, residual current circuit breaker (RCCB), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  | 0
12.1 | 40 A | 6 | No. | 2642 | 15852 | 2316 | 13896
13 | Supply, Installation, Testing and Commissioning of 1200 mm sweep, BEE 5 star rated, ceiling fan with Brush Less Direct Current (BLDC) Motor, class of insulation: B, 3 nos. blades, 30 cm long down rod, 2 nos. canopies, shackle kit, safety rope, copper winding, Power Factor not less than 0.9, Service Value (CMM/W) minimum 6.85, Air delivery minimum 215 CMM, 350 RPM (tolerance as per IS : 374- 2019), THD less than 10%, remote or electronic regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise=75 degree C (max.), insulation resistance more than 2 mega ohm, suitable for 230 V, 50 Hz, single phase AC Supply, earthing etc. complete as required. | 8 | Nos. | 2730 | 21840 | 2393 | 19144
14 | Providing and fixing M.S. fan clamp type I or II of 16 mm dia M.S. bar,bent to shape with hooked ends in R.C.C. slabs or beams during laying,including painting the exposed portion of loop,all as per standard design complete. | 8 | Nos. | 226 | 1808 | 198 | 1584
15 | S & F 40 amp to 63 amp rating 240 volts 'C' curve 10 kA MCB of following pole in the existing MCB DB complete with connection, testing & commissioning etc as reqd. ( legrand)
15.1 | Triple pole and neutral | 2 | Nos. | 3637 | 7274 | 3188 | 6376
16 | Supply fixing connecting & commissioning of following rating 3 pin Plug top as reqd complete.
16.1 | 15/16 Amp | 1 | Nos. | 151 | 151 | 132 | 132
17 | Laying UTP cable enhanced cat 5/cat 6 cable in existing steel conduit pipe/GI pipe/ raceway / RCC pipe as reqd. the cost shall also include numbering of networking wire from room to rack as reqd. (wire will be supplied by dept) | 800 | Mtr. | 23 | 18400 | 20 | 16000
18 | Fixing of RJ-45 modular box with cover plate or I/o box for internet on surface/ recessed cutting the wall making good the same as required. ( box and cover plate will be supplied by dept.) | 20 | Nos. | 96 | 1920 | 83 | 1660
19 | Providing and fixing DLP plastic trunking of size 105 mm x 50 mm without cover on surface as reqd. | 30 | Mtr. | 1157 | 34710 | 1014 | 30420
20 | Providing and fixing DLP plastic trunking of size 105 mm x 50 mm accessories on surface as reqd.
20.1 | PVC trunking full cover of size 85 mm size | 30 | Mtr. | 510 | 15300 | 447 | 13410
20.2 | End cap | 4 | Nos. | 231 | 924 | 202 | 808
20.3 | Internal angle. | 5 | Nos. | 638 | 3190 | 560 | 2800
20.4 | External angle | 5 | Nos. | 653 | 3265 | 573 | 2865
20.5 | flat angle | 1 | Nos. | 902 | 902 | 790 | 790
20.6 | cover joint | 10 | Nos. | 265 | 2650 | 232 | 2320
20.7 | Base joint | 60 | Nos. | 106 | 6360 | 95 | 5700
20.8 | separation partitions | 1 | Mtr | 305 | 305 | 267 | 267
20.9 | flat junction | 1 | Nos. | 1111 | 1111 | 974 | 974
21 | Supplying, installation DLP mini- trunking 32mm x 20mm and accessories white-system with independent cover- without central partion etc. as reqd.
21.1 | Mini- trunking | 100 | Mtr. | 268 | 26800 | 234 | 23400
21.2 | End cap left or right | 50 | Nos. | 179 | 8950 | 158 | 7900
21.3 | Internal/ external angle | 60 | Nos. | 173 | 10380 | 155 | 9300
21.4 | Flat angle | 40 | Nos. | 145 | 5800 | 127 | 5080
21.5 | Flat junction | 20 | Nos. | 171 | 3420 | 150 | 3000
22 | Supply and installation testing and commissioning of following LED fitting surface/recess mounted, IP20, with metallic CRCA powder coated housing cover highefficiency diffuser, THD less than10, power factor above 0.9.etc. as required Crompton make.
22.1 | 12W LED light 1"X1" or round cat no. LCDSPLN-R-12-CDL | 2 | Nos. | 1620 | 3240 | 1420 | 2840
22.2 | 36W LED light 2"X2" cat no. LCTLSNE-36-FO-CDL | 16 | Nos. | 6235 | 99760 | 5467 | 87472
23 | Supplying, fixing, connecting, commissioning and testing of the following luminaries light fixtures complete with all accessories and with lamp as required complete.
23.1 | LED tube light fitting (1 X 18 / 20 Watt. LED) surface mounting luminares | 2 | Nos. | 1030 | 2060 | 905 | 1810
24 | Supplying and fixing following size/ modules, Plastic/ PVC box alongwith modular base & cover plate for modular switches in recess etc. as required. Make- legrand.
24.1 | 1/2 module (75mm X 75mm) | 8 | Nos. | 403 | 3224 | 353 | 2824
24.2 | 3 module (100mm X 75mm) | 8 | Nos. | 443 | 3544 | 388 | 3104
24.3 | 4 module (125mm X 75mm) | 1 | Nos. | 478 | 478 | 421 | 421
24.4 | 6 module (200mm X 75mm) | 3 | Nos. | 541 | 1623 | 474 | 1422
24.5 | 8 module (125mm X 125mm) | 2 | Nos. | 598 | 1196 | 524 | 1048
25 | S & F of following size of steel flexible pipe alongwith the accessories on surface/open duct as required. .
25.1 | 20mm | 10 | Mtr | 81 | 810 | 71 | 710
25.2 | 25mm | 5 | Mtr | 95 | 475 | 84 | 420
25.3 | 32mm | 3 | Mtr | 116 | 348 | 103 | 309
26 | S&F, Copper tube / reducer/ lug terminals suitable for following size of conductor.
26.1 | 6,10,16 mm | 30 | Nos. | 49 | 1470 | 45 | 1350
| Total DSR & MR Items |  |  |  | 498610 |  | 437185
| Without GST |  |  |  | 437185.445
| Add GST @ 18% |  |  |  | 78693.3801
| Total |  |  |  | 515878.8251
| Add contingency @3% |  |  |  | 15476.3648
| Grand Total Rs |  |  |  | 531355.1898
| Say Rs. |  |  |  | 531355